## Seismic Parameters
657/667 Mission Street
Project:
[6 empty] | By: | RK | Date: | 2021.02.17
Mechanical Equipment Anchorage
| Seismic Demand on Non-structural Components |  |  |  |  | Overturning Calculations - (LRFD Procedure)
ref: CBC, ASCE7
MOT = Ω0Fp*Hcg
| Site Class: | D |  |  |  | MR = (0.9-0.2SDS)Wp*D/2
| Ss = | 1.318 | g
| Fa = | 1.2 | ASCE7 Table 11.4-1
| SMS = | 1.5816 | g = Fa Ss
| SDS = | 1.0544 | g = 2/3 SMS
| IP = | 1.5 | importance factor (ASCE7 13.1.3)
Equation ASCE7 13.3-1
Legend
Fp =
Equipment > 400 lb base mount that needs to conform to ASCE 7 Chapter 13
| Equation ASCE7 13.3-2, upper bound |  |  |  |  | Equipment < 400 lb for base mount with c.g.c > 4 ft above floor, or > 20 lb with c.g.c > 4 ft above floor, that needs to conform to ASCE 7 Chapter 13
| Fp = 1.6 SDS Ip Wp = |  | 2.5306 | Wp
| Equation ASCE7 13.3-3, lower bound |  |  |  |  | Equipment < 400 lb for base mount with c.g.c < 4 ft above floor, or < 20 lb with c.g.c > 4ft above floor, are exempt per CBC 1616.10.15
| Fp = 0.3 SDS Ip Wp = |  | 0.47448 | Wp
Seismic Vertical Force
| Fpv = 0.2 SDS = |  | 0.21088
Fp
0.9Wp
H
D, distance
btwn anchors
T
Wp, equipment
weight
0.2SDSWp
Hcg
Ωo

## Calculation
Mathcad Automation Template
Headers highlighted in yellow are mandatory. Cells highlighted in orange are input cells, and can be customized per specific needs. | [5 empty] | Inputs must follow the syntax: <input_name>_input(<unit>)
Text in blue are user input information. Fill out each row with the proper info. | [5 empty] | Note: use underscores instead of spaces. Headers without units will be processed as unitless.
eqpt_name | eqpt_number | mounting_location | project_number | eqpt_tags | tags | w_p_input(lb) | s_ds_input | a_p_input | r_p_input | i_p_input | z_input | h_input | capital_a_input(in) | capital_b_input(in) | a_input(in) | b_input(in) | capital_h_input(ft) | omega_input | factor_input
Anesthesia Machine | 1234 | Wall, Floor | 1111 | None | Medical, ICU, something | 335 | 1.121 | 1 | 2.5 | 1.5 | 0 | 75 | 30 | 20.5 | 1.5 | -1.5 | 74.25 | 2.5 | 0.66667
Warming Cabinet | 1234 | Floor | 1111 | None | Medical | 137 | 1.121 | 1 | 2.5 | 1.5 | 3 | 75 | 30 | 21.5 | 1.5 | -3.5 | 24.5 | 2.5 | 0.66667
Surgical Scrub Sink | 1234 | Wall | 1111 | None | Medical | 295 | 1.121 | 1 | 2.5 | 1.5 | 4 | 75 | 64 | 28 | 1.5 | -3.5 | 39.5 | 2.5 | 0.66667
Retractable Ceiling Column | 1234 | Ceiling | 1111 | None | Medical | 800 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
[8 empty] | w_p_input(lb) | z_input | h_input | a_p_input | r_p_input | omega_input |  |  | capital_h_input(ft) | capital_a_input(in) | capital_b_input(in) |  |  |  | CG_Y OUTPUT
[32 empty] | LRFD | ASD
FS | Equipment |  |  |  |  | Mount | Base | Wp | z | h | ASCE 7-10, Table 13.5 or 13.6 |  |  |  |  | D ("A") | L ("B") | a | b | H | h1 | Hcg | ASCE 7, 13.3.1.1 | [5 empty] | Ω0MOT | MR | MOT/ | Force per Support
Item | Description |  |  |  |  | Type | Material | (lb) | (ft) | (ft) | ap | Rp | Ω0 | SDS | IP | (in) | (in) | (in) | (in) | (in) | (in) | (in) | Fp / Wp | Fp_max / Wp | Fp_min / Wp | Fp / Wp | Fp (lb) | Ω0Fp (lb) | (lb*in) | (lb*in) | MR | Ω0T (lb) | Ω0T (lb)
NO INPUT HERE
EQ1 | AMSCO 400 Sterilizer |  |  |  |  | Ceiling |  | 4700 | 1 | 2 | 1 | 2.5 | 2 | 1.0544 | 1.5 | 32.25 | 50 | 2 | 2 | 60 |  | 51.3333 | 0.50611 | 2.5306 | 0.47448 | 0.50611 | 2378.7264 | 4757.4528 | 244215.9104 | 68208.75 | 3.5804 | 5457.5864 | 3820.3105
EQ2 | AMSCO 7053HP Washer |  |  |  |  | Base |  | 1336 | 1 | 2 | 1 | 2.5 | 2 | 1.0544 | 1.5 | 24.26 | 45 | 2 | 2 | 60 |  | 51.3333 | 0.50611 | 2.5306 | 0.47448 | 0.50611 | 676.1656 | 1352.3313 | 69419.6716 | 14585.112 | 4.7596 | 2260.2869 | 1582.2008
EQ3 | AMSCO 50 3-Bay Sink (empty) |  |  |  |  | Base |  | 380 | 1 | 2 | 1 | 2.5 | 2 | 1.0544 | 1.5 | 16.25 | 34 | 1 | 2 | 60 |  | 51.3333 | 0.50611 | 2.5306 | 0.47448 | 0.50611 | 192.3226 | 384.6451 | 19745.1162 | 2778.75 | 7.1058 | 1044.0841 | 730.8588
EQ3 | AMSCO 50 3-Bay Sink (filled) |  |  |  |  | Wall |  | 1690 | 1 | 2 | 1 | 2.5 | 2 | 1.0544 | 1.5 | 16.25 | 70 | 2 | 1 | 60 |  | 51.3333 | 0.50611 | 2.5306 | 0.47448 | 0.50611 | 855.3293 | 1710.6586 | 87813.8061 | 12358.125 | 7.1058 | 4643.4265 | 3250.3986
1234 | Anesthesia Machine |  |  |  |  | Wall, Floor |  | 335 | 0 | 75 | 1 | 2.5 | 2.5 | 1.0544 | 1.5 |  |  | 1.5 | -1.5 | 74.25 |  | 51.3333 | 0.25306 | 2.5306 | 0.47448 |  | 158.9508
1234 | Warming Cabinet |  |  |  |  | Floor |  | 137 | 3 | 75 | 1 | 2.5 | 2.5 | 1.0544 | 1.5 |  |  | 1.5 | -3.5 | 24.5 |  | 51.3333 | 0.2733 | 2.5306 | 0.47448
1234 | Surgical Scrub Sink |  |  |  |  | Wall |  | 295 | 4 | 75 | 1 | 2.5 | 2.5 | 1.0544 | 1.5 |  |  | 1.5 | -3.5 | 39.5 |  | 51.3333 | 0.28005 | 2.5306 | 0.47448
1234 | Retractable Ceiling Column |  |  |  |  | Ceiling |  | 800 | 15 | 75 | 1 | 2.5 | 2.5 | 1.0544 | 1.5 |  |  | 14 | 14 | 45 |  | 51.3333 | 0.35428 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
[14 empty] | 1.0544 | 1.5 | [6 empty] | 51.3333 | 0 | 2.5306 | 0.47448
Note on F5: Owner: Information attributed to the specific equipment. This will be stored in the database if indicated using the software
Note on K5: Owner: Importance factor.
Note on N5: Owner: Equipment width per diagram.
Note on O5: Owner: Equipment depth per diagram.
Note on P5: Owner: Distance from edge of equipment to mounting location along width axis per diagram.
Note on Q5: Owner: Distance from edge of equipment to mounting location along depth axis per diagram.
Note on R15: Owner: Equipment width per diagram.
Note on S15: Owner: Equipment depth per diagram.
Note on I18: Kuo, Richard: ASCE 7-10, 13.1.4 Exempt from Anchorage calc: - Floor mounted Wp <400lb and CG <4' - Wall-mounted or suspended <20 lb (or 5 lb/ft)
Note on N19: Kuo, Richard: Ωo = 1 for all non concrete anchorage; Ωo <> 1 for concrete anchorage per ASCE7-10 Table 13.6-1

## preview_images
Mounting Location | Preview image
wall
floor
wall,floor
ceiling