## values
Mathcad Automation Template
Headers highlighted in yellow are mandatory. Cells highlighted in orange are input cells, and can be customized per specific needs.
Text in blue are user input information. Fill out each row with the proper info.
eqpt_name | mounting_location | project_number | tags | w_p_input(lb) | s_ds_input | a_p_input | r_p_input | i_p_input | z_input | h_input | capital_a_input(in) | capital_b_input(in) | a_input(in) | b_input(in) | capital_h_input(ft) | omega_input | factor_input
Infraled Single (1 light) | Ceiling | EL 2A | Light, Exam/Procedure, Single, Ceiling, Recessed | 335 | 1.121 | 1 | 2.5 | 1.5 | 0 | 75 | 30 | 20.5 | 1.5 | -1.5 | 74.25 | 2.5 | 0.66667
AMSCO 24 inch Glass Doors | Floor | ME 2B | Cabinet, Warming, Dual, Freestanding | 381 | 1.121 | 1 | 2.5 | 1.5 | 3 | 75 | 30 | 21.5 | 1.5 | -3.5 | 24.5 | 2.5 | 0.66667
AMSCO Premium 24 inch Glass Doors | Floor | ME 2C | Cabinet, Warming, Dual, Freestanding | 142 | 1.121 | 1 | 2.5 | 1.5 | 4 | 75 | 64 | 28 | 1.5 | -3.5 | 39.5 | 2.5 | 0.66667
6060 Green (6 Cap.) | Floor | ME 3B | Rack, Cylinder, Floor | 13 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
Omnicell XT One-cell Cabinet | Floor | MS 1A | Dispenser, Medication, Host (main) | 335 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
Omnicell XT Quarter-Height Cabinet | Ceiling | MS 1C | Rack, Cylinder, Floor | 180 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
REF4P ADA Performance Plus Glass Door | Floor | RF 1C | Refrigerator, Medical Grade, Undercounter | 170 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
REF5 Medical Grade | Floor | RF 1D | Refrigerator, Medical Grade, Undercounter | 186 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
REF2-PR Medical Grade Patient Room | Floor | RF 1L | Refrigerator, Medical Grade, Undercounter | 73 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
FFHT1835VS (18.3 cu. Ft./Stainless Steel) | Floor | RF 2C | Refrigerator, Domestic with freezer | 164 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
Symphony Plus 25CI425A-S | Ceiling | RF 4 | Ice Machine, Dispenser, Nugget, Contertop | 213 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
Innowave WL 270 (formerly ChillerGF) | Floor | WC 1 | Dispenser, Water, Filtered | 60 | 1.121 | 1 | 2.5 | 1.5 | 15 | 75 |  |  | 14 | 14 | 45 | 2.5 | 0.66667
Note on D5: Owner: Information attributed to the specific equipment. This will be stored in the database if indicated using the software
Note on I5: Owner: Importance factor.
Note on L5: Owner: Equipment width per diagram.
Note on M5: Owner: Equipment depth per diagram.
Note on N5: Owner: Distance from edge of equipment to mounting location along width axis per diagram.
Note on O5: Owner: Distance from edge of equipment to mounting location along depth axis per diagram.

## preview_images
Mounting Location | Preview image
wall
floor
wall,floor
ceiling